OFFICE OF THE

NAGALAND ELECTRICITY REGULATORY COMMISSION (NERC)

NAGALAND : KOHIMA

Old MLA Hostel Complex,

Nagaland : Kohima -797001

Tel: (0370) 2292101(O) / 2241592(R)

Fax: 2292104 (O); www.nerc.org.in

e-mail: nerc_kohima@yahoo.com

N O T I F I C A T I O N

Dated Kohima, the  31st Jan ‘12

No.NERC/REGN/2012(A): In exercise of the powers conferred by sections 181 (2) (z a) and (z b) read with section 57  and 59 of the Electricity Act, 2003 (36 of 2003), the Nagaland Electricity Regulatory Commission (NERC), Kohima hereby makes the following regulations regarding the Distribution and Transmission Standards of performance.

CHAPTER - 1

GENERAL

1.1	Short Title, Commencement and Interpretation

- These Regulations may be called Nagaland Electricity Regulatory Commission (Standards of Performance for the Distribution and Transmission of the Licensee) Regulations, 2012.

- These Regulations shall be applicable to all licensees engaged in distribution and transmission of electricity in the State of Nagaland.

- These Regulations shall extend to the whole of the State of Nagaland.

- These Regulations shall come into force from the date of their notification in the official Gazette of Nagaland.

1.2	Definitions

In these Regulations, unless the context otherwise require:

"Act" means the Electricity Act, 2003 (Central Act No. 36 of 2003);

“Applicant” means a person, company, firm or establishment who makes an application for supply of electricity, increase or reduction in contract demand / sanctioned load, change of name, disconnection or restoration of supply or termination of agreement, as the case may be, in accordance with the provisions of the Act and the rules and regulations made there under;

“Authorized Representative” refers to all officers, staff or representatives of the Distribution and Transmission licensees, discharging functions under the general or specific authority of such Licensees;

“Availability” in relation to a transmission system in a given period means times in hours during which the transmission system is capable to transmit electricity at its rated voltage from the supply point to the delivery point and shall be expressed in percentage of total hours in a given period;

"Area of supply" means the area within which a distribution licensee is authorized  by his License to supply electricity;

"Commission" means Nagaland Electricity Regulatory Commission;

"Consumer" means any person who is supplied with electricity for his own use by a licensee or the Government or by any other person engaged in the business of supplying electricity to the public under this Act or any other law for the time being in force and includes any person whose premises are for the time being connected for the purpose of receiving electricity with the works of a licensee, the Government or such other person, as the case may be.

The term shall also includes person who have applied for an electrical connection, persons whose supply have not yet connected even after connection have been provided or whose electricity has been disconnected for non payment of dues etc, but whose connecting service lines/electrical apparatus has not been physically disconnected or whose agreement has not been terminated;

“Distribution Licensee” means a Licensee authorized by the Commission to operate and maintain a distribution system for supplying electricity to the consumers in his area of supply;

“Distribution System” means the system of wires and associated facilities between the delivery points on the transmission lines or the generating station connection and  the point of connection to the installation of the consumers;

"EHV/EHT" means Extra High Voltage/Extra High Tension (voltage level above 33,000 volts);

"Electricity Supply Code" means the Nagaland State Electricity Supply Code, approved and as amended from time to time by the Commission;

“Fuse-off call” refers to a complaint by an individual consumer involving restoration of supply as per directions given in clause 6.1 of the Regulation;

“Grievance” means a complaint filed by the affected person;

“Grid” means the high voltage backbone system of inter – connected transmission lines, sub-stations and generating plants;

"Grid Code" means the grid code notified by the Commission for the State of Nagaland in accordance with the Section 86 (1) (h) of the Act;

“Harmonics” means a component of a periodic wave having frequency that is an integral multiple of the fundamental power line frequency of 50 Hz causing distortion to pure sinusoidal waveform of voltage or current, and as governed by IEEE STD 519- 1992, namely “IEEE Recommended Practices and Requirements for Harmonic Control in Electrical Power Systems” and corresponding standard as may be specified by the Commission from time to time;

"HV/HT" means High Voltage/High Tension (voltage level above 650 volts but does not exceed 33,000 volts) under normal conditions;

“IEGC” means the Indian Electricity Grid Code approved by Central Electricity     Regulatory Commission (CERC) and shall include any Grid Code specified by Central Commission under clause (h) of sub-section (1) of section 79 of the Act;

"Licensee" means a person who has been granted a License by the Commission under section 14 of the Act and includes a deemed licensee;

"LT" means Low Tension voltage does not exceed 400 volts under normal conditions;

“NERLDC” means North-East Regional Load Despatch Centre;

“Rules” means the Indian Electricity Rules, 1956 and/or any other rules made under  the Act;

“Rural areas” means any area or areas comprising a village or a group of villages, as defined under the Constitution (Seventy-Third Amendment) Act, 1992;

"State" mean the State of Nagaland;

“SLDC” means the Load Dispatch centre to be established under sub-section (1) of Section 31 of the Act by the State Government of Nagaland and includes State Load Dispatch Centre, if any, already functioning in the State to ensure integrated operations of the power system in the state;

“State Transmission Utility” means the Government Company specified as such by the State Government under sub-section (1) of the Section 39 of the Act;

“Transmission Licensee” means a licensee authorized to establish or operate transmission lines by the Commission and includes State Transmission Utility and any of its successor entity under the provisions of section 131 of the Act;

“Transmission System” means a line with associated sub-section or a group of lines inter-connected together along with associated sub-station;

“Towns and cities” means areas other than Rural Areas;

Words and expressions used but not defined herein shall have meaning assigned to them in Electricity Act, 2003, Indian Electricity Grid Code, Electricity Grid Code and Indian Electricity Rules, 1956.

1.3	Objective

- The standards specified in these regulations shall serve as guidelines for Distribution Licensee to operate their Distribution System in an efficient, reliable, coordinated and economical system of electricity distribution and retail supply.

- The standards specified for transmission in these Regulations shall serve as guidelines for State Transmission Utility to operate the Intra – State Transmission System for providing an efficient, reliable, coordinated and economical system of electrical supply and Transmission.

The objectives of these standards are:

- to ensure that the Distribution System meets a minimum standard of      performance laid down in these regulations;

- to ensure that the grid performance meets minimum standards essential for the users system demand and purpose of functioning of equipment;

- to ensure that the Users design their systems and equipment to meet the

standards;

(d) to ensure the quality and quantity of supply of power to meet the

requirements of the consumers.

  - Guaranteed and overall standards of performance

The Standards of Performance are classified under the following two categories.

- Guaranteed Standards

- Overall Standards

- The standards specified in chapter – 4 and 6 shall be the Guaranteed Standards of Performance for Distribution and Transmission respectively being the minimum standards of service that a licensee shall achieve and maintain in the discharge of his obligations as a licensee.

- The standards specified in chapter – 5 and 7 shall be the Overall Standards of Performance for Distribution and Transmission which the licensee shall seek to achieve in the discharge of his obligation as a licensee.

- The Commission may from time to time add, alter, vary, modify a amend to the contents, of the chapters – 4, 5, 6 and 7, by a general or specific order passed by the Commission.

  - Compensation in case of under performance

(A) Distribution System:

- If a licensee fails to meet the Standards of performance specified in chapter – 4 of this regulation, without prejudice to any penalty, which may be imposed, he shall be liable to pay such compensation to the affected consumer through a rebate in the bill, upon written claim filed by any affected person. This rebate shall be admissible at a rate determined by the Commission in Appendix to such consumers as have regularly paid their bills and shall not exceed 10% of monthly bill or Rs. 100/- whichever is less.

- The licensee shall compensate the person(s) affected not later than ninety days from the date of determination.

- All payments of compensation determined by the Commission be made by way of adjustment against bills for supply of electricity.

- The compensation claims should be made by aggrieved consumer within two months time from the violation of the standards by the licensee.

- The compensation shall be payable to a consumer only in such cases where such consumer has paid in full, the last amount billed to him by the licensee.

- The licensee shall not be liable to pay compensation if it gets delayed in providing due services to the consumer due to non-accessibility of the premises and the licensee proves that it had served due notice, to consumer.

- The licensee shall maintain the record of compensation payable under sub-clause (1) above showing the name and address of affected person, amount of compensation payable and actually paid, mode of adjustment of compensation in bill as per sub-clause (2) in each case. The licensee on demand shall furnish such record to the Commission.

- Transmission System:

(1) The Licensee from the date as  specified by the  Commission by an  Order issued

in this behalf be liable to pay to the affected User(s) of the State Transmission System, the compensation as may be determined by the Commission by an order for the Licensee’s failure to meet the Guaranteed Standards of Performance specified in Chapter – 6.

- While  determining  the  compensation  to  the  affected  User(s)  the Commission

shall give a reasonable opportunity to being heard to the concerned Licensee and

all affected User(s). The  Commission  may  demand such  additional information,

evidence and summon records, logged data from the concerned Licensee and/or

affected User(s) for determination of compensation.

(3) The Licensee  concerned  shall  pay  the  compensation  determined  as  referred

in  sub - clause (1) above  within  ninety  days  of  the  failure of  the  Guaranteed

Standards of Performance.

  - Reporting on Standards of Performance

(A) For Distribution:

- For Guaranteed Standards, the licensee shall furnish to the Commission, in a report for every quarter and in a consolidated annual report, the following information;

- The levels of performance achieved by the licensee with reference to the standards specified in chapter – 4 to these Regulations.

- The number of cases in which compensation was paid under clause 5 above, and the aggregate amount of the compensation payable and amount paid by the licensee.

- The measures taken by the licensee to improve performance in the areas covered by Guaranteed Standards and licensee’s assessment of the targets to be imposed for the ensuring year.

- The quarterly reports under sub-clause (1) shall be furnished to the Commission within 15 days of the close of the quarter and the annual report under the said sub-clause (1) shall be furnished to the Commission within 30 days of the close of the financial year.

- For Overall Standards, each Licensee shall furnish to the Commission, in a report for every quarter and in a consolidated annual report, the following information;

- The level of performance achieved with reference to the standards specified in chapter - 4 to this Regulation.

- The measures taken by the licensee to improve performance in the areas covered by Overall Standards and Licensee’s assessment of the targets to be imposed for the ensuring year.

- The Quarterly reports under sub-clause (3) shall be furnished to the Commission within 15 days of the close of the quarter and the annual report under the said sub-clause (3) shall be furnished to the Commission within 30 days of the close of the financial year.

(B) For Transmission:

  - State Transmission Utility shall furnish to the Commission an half yearly report in the Format - 5, by October 31st and April 30th of each year on actual performance viz, is the performance standards laid down in these standards as modified from time to time.

  - The report shall contain all parameters irrespective of whether such parameters are applicable during the current reporting period.

  - The State Transmission Utility shall maintain the base data like Log Sheet, Complaint Registers and Interruption Register and relevant load flow studies in respect of system security etc. at sub-station level for compilation of monthly report at circle level. The consolidation report shall be based on circle – wise compilation for whole State Transmission Utility. The circle – wise compilation and base data at sub-station level shall be subject to its scrutiny as considered necessary by the Commission.

  - For the purpose of this Regulation, this half-year periods would be as follows:

(a)	1st Half Year:	1st April to 30th September;

(b)	2nd Half Year:	1st October to 31st March.

1.6.1    The Commission may from time to time, modify the contents of  the Formats or add

new formats for additional information.

1.6.2   The Commission shall, at such intervals as it may deem fit and not inconsistent with the provisions of the Act, arrange for the publication of the information furnished by Licensees under this Regulations.

  - Exemption

- The standards of performance specified in these regulations shall remain suspended during Force Majeure condition such as war, mutiny, civil commotion, riot, terrorist strike, flood, cyclone, lighting, earthquake or other force and strike, lockout, fire affecting the licensee's installations and activities. All Force Majeure conditions should be reported to the Commission within 30 days from the date on which such condition first occurred.

- Non- Compliance of a standard contained in this Regulations shall not be treated as a violation, and the Licensee shall not be required to pay any compensation to affected consumer(s), if such violation is caused due to grid failure, a fault on the Licensee’s network or on account of instructions given by SLDC, over which the Licensee has no reasonable control.

- The Commission may by a general or special order issued for the purpose and after hearing the Licensee and the affected consumer group release the Licensee from the liability to compensate the consumers for any default in the performance of any standard if the Commission is satisfied that such default is for reasons other than those attributable to the Licensee and further that the Licensee has otherwise made efforts to fulfill his obligations.

1.8	Issue of orders and practice directions

- Subject to the provisions of the Electricity Act 2003 (36 of 2003) and these regulations, the Commission may, from time to time, issue orders and practice directions in regard to the implementation of the regulations and procedures to be followed and various matters, which the Commission has been empowered by this Regulations to specify or direct.

- In particular, the Commission may authorize the Commission staff or any         independent agency to conduct periodical checks, monitor the compliance of the Standards by the licensee and report to the Commission.

  - Power to remove difficulties

If any difficulty arises in giving effect to any of the provisions of these regulations, the Commission may, by general or special order, do or undertake or direct the Licensees to do or undertake things, which in the opinion of the Commission are necessary or expedient for the purpose of removing the difficulties.

1.10	Power to Amend

- The Commission may, at any time add, vary, alter, modify or amend any provisions of these regulations.

- The Commission in consultation with the Licensee shall review these standards once in every two years or more frequently as may be required, if considered necessary. These Regulations shall however continue to be in force till it is modified based on such review.

1.11	Savings of Inherent Power of the Commission

- Nothing in these Regulations shall be deemed to limit or otherwise affect the inherent power of the Commission to make such orders as may be necessary to meet the ends of justice or to prevent abuses of the process of the Commission.

- Nothing in these Regulations shall bar the Commission from adopting in conformity with the provisions of the Act a procedure, which is at variance with any of the provisions of these Regulations, if the Commission, in view of the special circumstances of a matter or class of matters and for reasons to be recorded in writing, deems it necessary or expedient for dealing with such a matter or class of matters.

- Nothing in these Regulations shall, expressly or impliedly, bar the Commission dealing with any matter or exercising any power under the Act for which no Regulations have been framed, and the Commission may deal with such matters, powers and functions in a manner it thinks fit.

- Nothing in these regulations shall affect the rights and privileges of the consumers under any other law including the Consumer Protection Act, 1986.

1.12	Other Statutes

These Regulations should be read with relevant provisions of the Act and the Grid Code and Electricity Supply Code for Nagaland notified by the Commission as may be applied.

CHAPTER – 2

SAFETY

  - The construction, operation and maintenance of the distribution lines shall be carried out strictly in accordance with the Indian Electricity Rules, 1956 and other safety standards as may be in force from time to time according to the Section 53 of the Electricity Act, 2003.

  - The Licensee shall develop its own Operation and Maintenance manual (including safety Regulations) taking into consideration the safety requirements for the construction, operation and maintenance of electrical plants and electrical lines.

  - The Licensee shall take all necessary actions to spread awareness among the consumers for safe usage of the electricity.

  - The grounding provided for the equipment and lines and earthing grid for substations shall be in accordance with IS: 3043 - Code of Practice for Earthing and it should also be maintained in a sound and healthy state at all times. The Licensee shall take all necessary steps for testing of the same and maintain the record of each test in accordance with Rules- 32, 51, 61, 62, 67, 69, 88(2) and 90 of the Indian Electricity Rules, 1956.

  - The Licensee shall ensure that no live parts of any overhead line or Distribution transformer are so exposed as to cause danger. The Licensee shall follow the provisions under Rules 50(2) of Indian Electricity Rules, 1956. The Licensee shall also adhere to the provisions under Rules 77, 78, 79 and 80 of Indian Electricity Rules, 1956 regarding clearances of overhead lines with respect to ground, trolley wires and buildings etc.

  - Leakage current means difference between phase current and return path. The Licensee shall take necessary steps to measure leakage current at various points in the system.

  - The earth wires and the earth electrodes provided in the Distribution System shall be maintained in good condition to ensure instantaneous operation of the Protective Equipment, either a Fuse or a Circuit Breaker as the case may be, in case of accidental snapping of conductor. In case of failure in the operation of the protective system during any accidental snapping of conductors, the circuit shall be de-energised manually immediately after it comes to the notice of the concerned employee of the Licensee. A detailed investigation shall be done to determine the cause for non-operation of the protective system and remedial measures shall be taken promptly.

  - The Licensee may disconnect supply to such consumer, in the event of any   consumer’s non-compliance which persists even after due notice, of any specific  condition or direction if such non-compliance can reasonably be expected to affect  system operations and safety. In cases of emergency, disconnection may be  effected immediately in the interest of system operations and safety. The connection should be immediately restored as soon as the originating causes leading to the disconnection are removed or rectified.

  - Accidents: The records of all the fatal electrocution accidents shall be maintained along with the investigation report of the Chief Electrical Inspector (CEI). A copy of the action taken report with regard to the procedure prescribed by the CEI for safety measure for avoiding recurrence of such fatal accidents shall be submitted to the Commission every six months i.e., by 31st October and 30th April of each year.

# CHAPTER  - 3

HANDLING OF COMPLAINTS

  - The Licensee is required to maintain standards of performance for supply of electricity to all consumers in the manner prescribed hereinafter. The limits prescribed in these standards refer to the maximum time permissible for performance of different activities of consumer services. It shall be the endeavour of the licensee to provide the best possible services well within the time limits specified in these Regulations.

  - The Licensee shall register every complaint made by a consumer, either verbally or  in writing, regarding failure/interruption of power supply, quality of power supply,  meters/meter boxes/metering system’s service line, payment of bills and other  services relating to power supply, in a register / registers or in electronic format to  be maintained for this purpose. A unique number shall be allotted to each complaint. This complaint number shall be conveyed to the consumer except in the case of postal complaints received. However the consumer may, subsequent  to the delivery of postal complaint, inquire regarding the complaint number/ status  telephonically or in person. The number shall be communicated to the complainant  in such a case. In case of major failure of supply due to tripping of EHV or failure of  upstream power systems, the reason needs to be communicated to the consumer in addition to the likely restoration time. The Licensee shall ensure redressal of all complaints promptly.

  - Complaints in respect of supply of electricity covering metering, billing and payment, shall be made at specified offices of the Licensee. Licensee shall convey information of the name of office(s), address(s) and telephone numbers where the consumer can lodge complaints, with the electricity bills and also display it at the sub-division offices or equivalent distribution unit designated by whatever name. If the phone services for recording complaints, if outsourced by the Licensee, the phone numbers of such call centre shall be displayed in electricity bills and sub-divisional offices. The Licensee shall also endeavor to publicize these contact details through local newspapers / TV / Radio.

  - The office where a complaint is registered shall dispose it of and if any      instruction/sanction is to be obtained from a higher authority, it shall be obtained by  the Licensee’s staff/Officers. The complainant is not required to approach such      higher authority. Similarly, in case an outsourced phone service is engaged for   registering the complaints, such centre itself shall forward the complaints to the      concerned officer. The Licensee shall ensure proper compliance by the outsourced      service by arranging visits of its officers to such centers to streamline responses.

  - Grievances regarding non-registration of complaints and failure to perform within the time limits and/or to meet the performance targets, as specified in these Regulations, shall be made to the concerned officer in-charge of the division or to equivalent distribution unit designated by any other name. In case of unsatisfactory disposal of grievances/complaint a reference should be made to the officer in-charge of the circle or equivalent similar functionary by whatever name designated.

  - The Licensee shall provide a toll free telephone connection at Central Fuse off Call centre of Licensee’s Head Quarter to receive consumer complaints from the consumers situated in any area of the Licensee.

  - Every authorized representative of the Distribution Licensee shall visibly display his name-tag and, if so required by such consumer, produce for scrutiny, proof of identity and authorization of Distribution licensee for the purpose of any interaction with a consumer.

  - The Distribution Licensee shall maintain, in every town and city within the area of supply, at least one consumer service centre which shall be open for not less than eight (8) hours a day, on all days of the week, for essential services to be provided to consumers and with a collection facility for collection of revenues from consumers.

# CHAPTER – 4

# GUARANTEED STANDARDS OF PERFORMANCE FOR DISTRIBUTION

## Restoration of Power Supply

- Fuse-off: The Licensee shall restore power supply in the case of normal fuse-off calls (replacing Horn Gap (HG) fuses or Low Tension (LT) fuses at the distribution transformer or at the consumer premises) within 6 working hours of receiving the complaint in towns and cities and within 24 working hours of receiving the complaint in rural areas. Individual fuse-off calls at consumer premises, wherever the fault is of such nature that it requires shutting down the power supply affecting other consumers also, shall not however be attended to between 5 PM and 8 AM except in case of essential services covered under the Essential Services Maintenance Act (ESMA).

- Overhead Line/Cable Breakdowns: In case of overhead line/cable breakdowns, the Licensee shall ensure restoration of power supply within 6 hours of occurrence of breakdown in towns and cities and within 24 hours of occurrence of breakdown in rural areas.

- Underground Cable Breakdowns: In case of breakdown of underground cable, the Licensee shall ensure restoration of power supply within 36 hours of occurrence of breakdown in towns and cities and within 72 hours of occurrence of breakdown in rural areas.

- Distribution Transformer failures: The Licensee shall restore supply in the case of distribution transformer failures by replacement of transformer within 48 hours of receiving the complaint in towns and cities and within 5 days of receiving the complaint in rural areas.

The Licensee shall make arrangement to keep reasonable number of spare

transformers with the operation units.

- Period of scheduled outages: Interruption in power supply due to scheduled outages, other than the load-shedding, for duration of more than one hour shall be notified by the Licensee at least 24 hours in advance through newspapers, local TV networks and such interruption and shall not exceed 12 hours in a day. In each such event, the Licensee shall ensure that the supply is restored by not later than 5:00 PM.

- Street Lights: The Licensee shall restore the street lights within 48 hours of receiving complaint subject to providing of the materials by the Corporation / Municipality.

## Quality of Power Supply

(1)  Voltage fluctuations

  - The Licensee shall maintain the voltages at the point of commencement of supply to a consumer within the limits stipulated hereunder, with reference to declared voltage:

    - In the case of Low Voltage, +6% and -6%;

    - In the case of High Voltage, +6% and -9%; and

    - In the case of Extra High Voltage, +10% and -10%.

  - On receipt of a voltage fluctuation complaint, the Licensee shall verify if the voltage fluctuation is exceeding the limits specified in sub-paragraph (i) above and if confirmed, the Licensee shall

- Ensure that the voltages are brought within the said limits, within 15 days of original complaint if no expansion/enhancement of network is involved;

- Resolve the complaint within 120 days, if up-gradation of distribution system is required :

Provided that where a substation is required to be erected to resolve such complaints, the Licensee shall, within one month of the receipt of such complaint, submit to the Commission a proposal for erection of the substation, together with the time required to complete erection and commissioning of such substation and get the same approved by the Commission:

Provided further that where such substation is covered in the Licensee’s investment plan approved by the Commission, the Licensee shall complete the erection and commissioning of the such substation within the time period specified in such investment plan.

Provided further that no compensation on account of voltage fluctuations shall be payable to industrial and agricultural consumers who do not provide capacitors to the prescribed extent.

(2) Harmonics

Harmonics is a sinusoidal voltage and current having frequency that are Integral multiple of the fundamental frequency. Many loads in power system produce current and voltages at frequencies in multiple of the fundamental frequency. These multiple frequency voltage and currents are called Harmonics and their ratio to the fundamental frequency is called Harmonic order. Harmonics affects system operation and reduces life of the equipments. Some types of loads like Induction & Arc Furnace, electromagnetic equipment such as X-ray machines etc produce harmonics in supply voltages.

The licensee shall monitor Harmonics at regular intervals at strategic points which it considers prone to Harmonic voltage generation and ask the user to comply with specific standards. Harmonic measurement shall conform to IEC Std: 1000-4-7 or IEE Std: 519. The Licensee shall take adequate measures to prevent harmonics induction in the distribution system from consumer load side equipments like Induction & Arc Furnace, electromagnetic equipment such as X-ray machines etc.

(2)  Neutral Voltage Displacement:

Unbalance in loads on three phases cause shifting of neutral from earth potential. Neutral displacement is applicable for transformers with ‘Star Point’ solidly grounded. Under “solidly” grounded conditions, the potential of neutral should be equal to earth i.e. zero. But in actual conditions, the earthing of the star point is imperfect and so the star to ground offers small resistance. This results in flow of negative sequence currents (because IR + IY + IB is not equal to zero, through neutral to ground), thereby causing shift of neutral from earth potential, which is the neutral voltage displacement.

Unbalance voltages and displacement of neutral result in decreased efficiency, negative torque, leakage currents, vibrations and overheating. Severe unbalance and neutral displacement could lead to malfunctioning of some equipments. Some types of loads like X-ray machines; electric traction; induction and arc furnace may induce unbalance in the supply voltages and shift the voltage of neutral from earth potential.

The Distribution Licensee shall ensure that the neutral point voltage of all the 33/11 kV and 11/0.4 kV transformers with respect to earth will not have potential greater than 2% and 5% respectively of the no load phase-phase voltage of the transformers.

- Frequency Deviation:

The frequency band specified in the IEGC is normal operating range for efficient system operation. The Licensee shall monitor the frequency to ensure that frequency remains within the limits specified in IEGC and deviation in frequency beyond IEGC target range shall be taken up with the SLDC for appropriate corrective measures.

| Target range as per IEGC |  |
| --- | --- |
| Upper Limit | 50.5Hz |
| Lower Limit | 49.0 Hz |

4.3	Complaints about meters

- The Licensee shall inspect and check the correctness of the meter within 7 working days of receiving the complaint in cities and towns and within 15 working days in rural areas and within 20 days in remote areas. If the meter is not working (stuck up, running slow, fast or creeping), the Licensee shall replace the meter at Licensee’s own cost, within 15 days thereafter.

- The Licensee shall replace at Licensee’s own cost the burnt out meters within 7 days of complaint if the burning of meter is due to causes attributable to the Licensee like high voltage, loose contacts, aging of meter, etc. If the meter is burnt due to causes attributable to the consumer such as tampering, defect in consumer’s installation, meter getting wet, connecting unauthorized additional load by the consumer, etc., the Licensee shall serve a notice to the consumer for recovery of cost of the meter within 7 days of detection and shall replace the meter within 7 days of receiving the payment from the consumer and after necessary corrective action is taken to avoid future damage to the meter.

4.4	Release of New connections/Additional Load

(1) Time frame for release of new connection

Regarding release of supply to new connections / additional load the relevant Regulations of the Electricity Supply Code shall apply. The Licensee shall release supply to an applicant within the limit specified below after receipt of the complete application, prescribed fees and charges and Security deposit.

(a) 	Cases where power supply can be provided from the existing network.

(i) L.T Connections

Urban area        -	10 working days

Rural area         - 	15 working days

Remote area	  -	20 working days

(ii) H.T Connections      -   	60 working days

(iii) E.H.T Connections -   	180 working days

(b) Cases where providing of power supply requires extension of lines.

(i) L.T Connections

Urban area  	 - 	42 working days

Rural area    	- 	50 working days

Remote area	-	90 working days

(ii) H.T Connections 	-

11 kv		-	100 working days

33 kv		-	120 working days

(c)	Cases where providing of power supply requires installation of transformer.

(i) L.T Connections (Other than agricultural connections)

Urban area  	- 	60 working days

Rural area   	- 	90 working days

Remote area	-	120 working days

(ii) Agricultural Connection

(a) Having approach road     	-     75 working days

(b) Having no approach road 	-     90 working days

(d) 	 Incase of application for new connection, where extension of supply requires erection and commissioning of new 33/11 KV substation, the distribution Licensee shall submit to the Commission within 30 days of receipt of such application, a proposal of erection of such 33/11 KV substation together with the time required for erecting and commissioning the substation, and get the same approved by the Government. The Licensee shall commence power supply to the applicant within the time period so approved by the Government.

Provided that if the substation is meant to extend supply to an individual consumer, the Licensee shall commence erection of the substation only after the receipt of necessary security from the applicant.

(e) Temporary Supply

(i)    Consumers  may  requisition  for  temporary  supply  for  construction  and  other

purposes in the prescribed application form.

(ii)	The Licensee may collect deposit covering the cost of effecting temporary service connection and the cost of expected energy consumption.

(iii)	 The  Licensee  shall  release  supply  on  the  date if required by the consumer in

case where Distribution lines are existing.

(iv) Where extension of distribution main is required the time schedule as mentioned

in para 4.4 shall apply.

(v) The Licensee shall refund the balance deposit, if any within three months from the

date of dismantling the temporary service connection, after adjustment of the dues

payable by the consumer.

(2)	Delay in Supply of Electricity to New Premises

  - If the Licensee cannot supply electricity within the scheduled period as per Regulation 4.4, he shall promptly intimate the applicant the likely date of supply and the reasons for delay.

  - The Licensee shall not, however, be held responsible for the delay, if any, in extending supply, if the same is on account of problems relating to statutory clearances, right of way, acquisition of land, or the delay in consumer’s obligation to obtain approval of Chief Electrical Inspector to Government for his High Tension or Extra High Tension installation, etc. over which Licensee has no reasonable control.

  - Additional period required on account of special circumstances mentioned above, shall be added to the normal period as per Regulation 4.4 i.e. the period within which the Licensee has to release new supply.

(3) Extension of Time Limit

    - The Licensee may approach Commission for extension of time specified above in cases where the magnitude of work requires more time, duly furnishing the details in support of such extension. Such request shall be soon after made, after the estimate is prepared.

    - The time limit shall be extended by the period by which the consumer delays to fulfill the following beyond the due date intimated by the Licensee: -

  - Payment of service connection charges and security deposit.

  - Certificate that the internal wiring / consumer’s electrical system including machinery, equipment and appliances are in good condition, comply with the standards including safety standards and the insulation resistance of the system is more than minimum stipulated value.

  - Agreement between the Licensee and the consumer is signed by the consumer.

  - Filing ownership certificate of the premises.

  - Settlement of dues if the applicant had availed supply of electricity earlier.

  - Providing of space for installation of transformer or metering equipment, if required.

- Waiting List

The Licensee should maintain a register of pending cases awaiting             new service connections.

## 4.5	Transfer of ownership and conversion of services

The Licensee shall give effect to transfer of ownership, change of category and conversion of the existing services from Low Tension to High Tension and vice-versa within the following time limits:

- Title transfer of ownership	     	-within 7 days of receipt of application

with necessary documents and

prescribed fee, if any.

(b) 	Change of category

(c) 	Conversion from Low Tension 	- within 30 days from the date of

single phase to Low Tension 		  payment of necessary charges by

3-phase and vice-versa 		  the consumer

(d) 	Conversion from Low Tension 	- within 90 days from the date of

to High Tension. 	  payment of necessary charges by  the

consumer.

Provided that in case of conversion from Low Tension to High Tension and vice-versa, the Licensee shall not be held responsible for the delay if the same is on account of delay in consumer’s obligation to obtain approval of Chief Electrical Inspector to Government, for such installation.

## Complaints about consumer’s bills

- The Licensee shall acknowledge the consumer’s complaint immediately, if received in person and within 2 working days, if received by post. The Licensee shall resolve the complaint regarding electricity bills within 24 working hours of its receipt, if no additional information is required to be collected and within 7 working days of receipt of complaint in case any additional information is required.

- In case the complaint is genuine and revision of bill already issued becomes necessary, the due date for payment of bill shall be reckoned from the date of revised bill for the purpose of disconnection of supply or for levy of additional charges for belated payment.

  - Reconnection of supply following disconnection due to non-payment of bills

The Licensee shall restore power supply to a consumer, whose supply has been disconnected due to non-payment of electricity bills, within 4 working hours of receipt of an application and production of proof of payment by the consumer in towns and cities, and within 12 working hours of application and production of proof of payment by the consumer in rural areas.

  - Complaints about consumer’s bills

- The Licensee shall acknowledge the consumer’s complaint immediately, if received in person and within 2 working days, if received by post. The Licensee shall resolve the complaint regarding electricity bills within 24 working hours of its receipt, if no additional information is required to be collected and with 7 working days of receipt of complaint in case any additional information is required.

- In case the complaint is genuine and revision of bill already issued becomes necessary, the due date for payment of bill shall be reckoned from the date of revised bill for the purpose of disconnection of supply or for levy of additional charges for belated payment.

### APPENDIX

GUARANTEED STANDARDS OF PERFORMANCE AND COMPENSATION TO CONSUMERS IN CASE OF DEFAULT

| Service Area | Guaranteed Standard Maximum time limit for rendering service |  | Compensation payable to affected consumers in case of violation of standards |
| --- | --- | --- | --- |
| Fuse-off |  |  |  |
| Cities and towns | Within 6 working hours |  | Rs.5/- per consumer for every 1 hour subject to maximum Rs. 50/- per day in each case of default. |
| Rural areas | Within 24 working hours |  | Rs.20/- per consumer per day subject to Rs. 50/- beyond one day. |
| Remote areas | Within 36 working hours |  | Rs.20/- per consumer per day subject to Rs. 50/- beyond one day. |
| Overhead Line/cable breakdowns |  |  |  |
| Cities and towns | Within 36 hours |  | Rs.10/- per consumer per day for delay beyond 24 hours, if the number of affected consumers are less than 50, and Rs. 5/- per consumers per day for affected consumers 50 or more subject to maximum Rs. 50/- per consumer. |
| Rural areas | Within 48 hours |  | Rs. 5/- per consumer per day for delay beyond three days subject to maximum Rs. 50/- per consumer. |
| Remote areas | Within 96 hours |  | Rs. 5/- per consumer per day for delay beyond three days subject to maximum Rs. 50/- per consumer. |
| Underground cable breakdowns |  |  |  |
| Cities and towns | Within 36 hours |  | Rs.10/- per consumer per day for delay beyond 24 hours, if the number of affected consumers are less than 50, and Rs. 5/- per consumers per day for affected consumers 50 or more subject to maximum Rs. 50/- per consumer. |
| Rural areas | Within 72 hours |  | Rs. 5/- per consumer per day for delay beyond three days subject to maximum Rs. 50/- per consumer. |
| Remote areas | Within 144 hours |  | Rs. 5/- per consumer per day for delay beyond three days subject to maximum Rs. 50/- per consumer. |
| Distribution Transformer failure |  |  |  |
| Cities and towns | Within 48 hours |  | Rs. 20/- per consumer/day for delay beyond 1day to maximum Rs. 100/- per consumer. |
| Rural areas | Within 5 days |  | Rs. 10/- per consumer/day for delay beyond 5 days to maximum Rs. 100/- per consumer. |
| Remote areas | Within 10 days |  | Rs. 10/- per consumer/day for delay beyond 5 days to maximum Rs. 100/- per consumer. |
| Period of Scheduled Outage |  |  |  |
| Maximum duration in a single stretch | Not to exceed 12 hours |  | Rs.100 in each case of default. |
| Restoration of supply | By not later than 5:00 PM |  |  |
| Voltage fluctuations |  |  |  |
| No Expansion/enhancement of network involved. | Within 15days |  | Rs.50 for each case of default. |
| Up-gradation of distribution system required | Within 120 days |  | Contd. on next page also for voltage fluctuation Rs.50 for each case of default |
| Erection of 33/11 kv Substation | Within the time period as approved by the Govt. |  | Rs. 50/- for each day default. |
| Meter complaints |  |  |  |
| L.T Consumers |  |  |  |
| Testing, checking & calibration for correctness of meter |  |  |  |
| Uraban Area | 7 days from lodging of complaint |  | Rs. 50/- per day for delay beyond 7 days subject to maximum Rs. 200/- per consumer. |
| Rural areas | Within 15 days |  | Rs. 50/- per day for delay beyond 15 days subject to maximum Rs. 200/- per consumer. |
| Remote areas | Within 20 days |  | Rs. 50/- per day for delay beyond 15 days subject to maximum Rs. 200/- per consumer. |
| Defective/ Stopped / Burnt, meter Replacement |  |  |  |
| Urban area |  |  |  |
| Replace not attributable to consumer | 7 days |  | Rs. 50/- per day for delay beyond specified period subject to maximum Rs. 200/- per consumer. |
| Where the cost of the meter is recoverable from the consumer | 15 days after the receipt of payment |  | Rs. 50/- per day for delay beyond specified period subject to maximum Rs. 200/- per consumer. |
| Where the consumer is required to supply the metering equipment | 15 days after supply of metering equipment payment |  | Rs. 50/- per day for delay beyond specified period subject to maximum Rs. 200/- per consumer. |
| Rural Area |  |  |  |
| - Replacement not attributable to consumer (b) Where the cost of the meter is recoverable from the consumer | 15 days 30 days after the receipt of payment |  | Rs. 50/- per day for delay beyond specified period subject to maximum Rs. 200/- per consumer. |
| Remote area |  |  |  |
| - Replacement not attributable to consumer (b) Where the cost of the meter is recoverable from the consumer | 30 days 45 days after the receipt of payment |  | Rs. 50/- per day for delay beyond specified period subject to maximum Rs. 200/- per consumer. |
| H. T. Consumers |  |  |  |
| Replacement of stopped/defective meter or related equipments | Within 7 days after receipt of complaint. |  | Rs. 100/- per day for delay beyond specified period subject to maximum Rs. 2000/- per consumer. |
| Where the cost of the meter is recoverable from the consumer | Within 15 days after receipt of complaint. |  | Rs. 100/- per day for delay beyond specified period subject to maximum Rs. 2000/- per consumer. |
| Where the consumer is required to supply the meter/equipment | 10 days after delivery of meter / equipment to Licensee. |  | Rs. 100/- per day for delay beyond specified period subject to maximum Rs. 2000/- per consumer. |
| Restoration of street lights |  |  |  |
| Cities and towns | Within 48 hours of receipt of complaint |  | Rs. 50/- per day. |
| Application of new connection/additional load |  |  |  |
| Connection feasible from existing network |  |  |  |
| Release of L.T,H.t & E.H.T Supply |  | Within time frame given at cl. 4.4(i) | Rs. 50/- for each day of default. |
| Network expension/enhencement required to release supply |  |  |  |
| Release of supply - Low Tension | Within time frame given at cl. 4.4(i) |  | Rs. 50/- for each day of default |
| Release of supply - High Tension 11 KV | Within time frame given at cl. 4.4(i) |  | Rs. 50/- for each day of default |
| Release of supply - High Tension 33 KV | Within time frame given at cl. 4.4(i) |  | Rs. 50/- for each day of default |
| Release of supply - Extra High Tension | Within time frame given at cl. 4.4(i) |  | Rs. 50/- for each day of default |
| Erection of substation required for release of supply | Within the time period approved by the Commission |  | Rs. 50/- for each day of default |
| Transfer of ownership and conversion of service |  |  |  |
| Title transfer of ownership | Within 7 days along - with necessary documents, clearance of outstanding dues and prescribed fee, if any |  | Rs. 50/- for each day of default |
| Change of category | Within 7 days along - with necessary documents, clearance of outstanding dues and prescribed fee, if any |  |  |
| Conversion from LT 1 –ph to LT 3 – ph and vice versa | Within 30 days of payment of charges by the consumer |  |  |
| Conversion from LT to HT and vice versa | Within 90 days of payment of charges by the consumer |  |  |
| Resolving of complaints on consumer’s bill |  |  |  |
| If no additional information is required | Within 24 working hours of receipt of complaint |  | Rs. 50/- for each day of default |
| If additional information is required | Within 7 working hours of receipt of complaint |  |  |
| Reconnection of supply following disconnection due to non – payment of bills |  |  |  |
| Cities and Towns | Within 4 working hours of production of proof of payment by consumer |  | Rs. 50/- for each day of default |
| Rural Areas | Within 12 working hours of production of proof of payment by consumer |  |  |
| Remote Areas | Within 24 working hours of production of proof of payment by consumer |  |  |

CHAPTER – 5

OVERALL STANDARDS OF PERFORMANCE FOR DISTRIBUTION

  - Fuse-off calls: The Licensee shall ensure rectification of fuse off calls rectified within the time limits prescribed under sub-paragraph 4.1 of chapter - 4. The Licensee shall achieve the Standard of Performance in at least 95% of the cases.

  - Line Breakdowns: The Licensee shall ensure restoration of power supply within the time limits prescribed in sub-paragraph 4.1 (2) of chapter - 4. The Licensee shall achieve this standard of performance in at least 95% of the cases.

  - Distribution Transformer Failures: The Licensee shall maintain the percentage of  failed distribution transformers replaced within the time limits prescribed in sub-paragraph  4.1 (4) of Chapter - 4 to the total distribution transformers failed not less than 95%.

  - Period of scheduled outages: As specified in the sub-paragraph 4.1 (5) of chapter 4, interruption in power supply due to scheduled outages, other than the load shedding, has to be notified in advance and shall not exceed 12 hours in a day and in each such event, the Licensee has to ensure that the supply is restored by 5:00 PM. The Licensee shall achieve both of these standards of performance in at least 95% of the cases

  - Street Light Faults: The Licensee shall as soon as possible attend to complaints relating to non-working of streetlights or not operating properly to the extent the matter lies within the purview of the Licensee. At least 90% of cases shall be complied within the prescribed time limit.

  - Frequency variations: The rated frequency of the system shall be 50.0HZ. The            Licensee shall achieve coordination with other network constituents such as State Transmission Utility, State Load Despatch Center and other distribution Licensees and Transmission Licensees in an endeavor to maintain the supply frequency within limits as per IEGC standards (Indian Electricity Grid Code).

  - Voltage Unbalance: In distribution system unbalance in supply voltages should be minimized such that it does not affect the performance of consumer’s equipment like motors and other gadgets connected to distribution supply system. Voltage unbalance is defined as the maximum deviation in voltage between two phases divided by average of the phase voltages of all three phases, expressed in terms of percent.

| Voltage Unbalance = | Deviation between highest and lowest phase voltage | x 100 |
| --- | --- | --- |
|  | Average voltage of three phases |  |

The Licensee shall ensure that the voltage unbalance does not exceed 3% at the point of commencement of supply. The voltage unbalance shall be measured at sub stations provided with measuring instruments having accuracy class within 1% limit.

  - Billing mistakes: The Licensee shall maintain the percentage of bills requiring modifications following complaints to the total number of bills issued, not greater than 0.2%. At least 99% of the cases related to billing mistakes should be resolved within prescribed time limit.

5.9 	Faulty meters: The Licensee shall maintain the percentage of defective meters to the total number of meters in service, at a value not greater than 3%. Atleast 95% cases in urban areas and 90% cases in rural areas should be resolved within prescribed time limit.

5.10 	Service Reliability: Reliability of the distribution system operated by the Licensee shall be computed on the basis of the number and duration of sustained interruptions in a year. In a power system, it may take a few minutes to restore power after transient faults or to reroute power in the network to restore supply to the affected area, where a large number of consumers are involved. Sustained interruptions of more than ten minutes duration shall be considered for judging the reliability of the system and temporary interruptions not exceeding ten minutes duration shall be ignored in computation.

Reliability standards of the Licensee shall be judged by the following two indices.

(a) Consumers Average interruption Frequency Index (CAIFI):

## Consumers average interruption frequency index, which shall be calculated by dividing the total number of sustained interruptions to consumers in a year by the total number of consumers served. An interruption in supply to a consumer shall be considered as one interruption to one consumer. In case of failure of a line or transformer, number of interruptions shall be equal to the number of consumers affected. The index shall be expressed as number of interruptions per consumer per year and shall be calculated annually.

CAIFI = ∑(I * K)

N

Where,

I	=	Number of interruptions exceeding 10 minutes at a time for the

voltage class.

K	=	Number of consumers whose power supply remained ‘off ’ as a

result of such interruption.

N	=	Total number of consumers in service at the beginning of year having

that class of voltage supply.

* Multiplication sign.

CAIFI shall be calculated for a sub-station, for a circle and for the Licensee as a              whole. The index shall be expressed in number of interruptions per consumer per              year.

(b) Consumer average Interruption Duration Index (CAIDI)

Consumers average interruption duration index, which shall be calculated by dividing the total minutes of sustained interruptions to supply to consumers in a year by the total number of consumers served. The index shall be expressed as number of minutes of interruption per consumer per year and shall be calculated annually.

CAIDI = ∑(P * K)

N

Where,

P	=	Duration of interruptions exceeding 10 minutes at a time for the

voltage class.

K	=	Number of consumers whose power supply remained “off” as a result

of such interruption.

N	=	Total Number of consumers in service at the beginning of year having

that class of voltage supply.

* Multiplication sign.

CAIDI shall be calculated for a sub-station, for a circle and for the Licensee as a         whole. The index shall be expressed in interruption of minutes per consumer per year.

While calculating the CAIFI and CAIDI indices, the following types of interruptions shall not be taken into account:

- Planned outages;

- Temporary interruptions of duration less than ten minutes;

- Outages due to failure of upstream power system including generation and transmission network;

- Outages due to Force Majeure reasons beyond the Licensee control like fire, earthquake, floods, storms and riots.

The Licensee shall compile above data at each sub-station for calculating reliability indices. The Licensee shall compile monthly data for each Circle to ascertain Circle wise reliability indices of the system.

The Commission shall fix benchmark for standards of reliability on the basis of data collected for one year and revise the levels to be achieved from time to time for ensuring improvement in the performance of the Licensee.

  - The Summary of Overall performance standards is as follows:

| Service area | - Overall Standard of Performance |
| --- | --- |
| fuse-off calls | - At least 95% calls received should be rectified within prescribed time limits in both Cities and Towns and in Rural areas. |
| Line Breakdowns | - At least 95% of cases resolved within time limit in both Cities and Towns and in Rural areas. |
| Replacement of Distribution Transformer failed | At least 95% of failed DTRs to be replaced within prescribed time limits in both Cities and Towns and in Rural areas. |
| Period of scheduled outage | At least 95% of cases resolved within time limit. |
| Maximum duration in a single stretch |  |
| Restoration of supply by 5:00 PM |  |
| Street Light Faults | At least 90% cases should be complied within prescribed time limits. |
| Rectification of line faults |  |
| Replacement of fused/defective unit |  |
| Frequency variations | To maintain supply frequency within range as per IEGC. |
| - Voltage Unbalance | Maximum of 3% at point of commencement of supply. |
| Percentage billing mistakes | Not exceeding 0.2% of total bills issued At least 99% of cases resolved within time limit. |
| Percentage faulty meters | Not exceeding 3% of existing meters At least 95% of cases in urban areas and 90% of cases in rural areas resolved within time limit. |
| Reliability Indices | To be laid down by the Commission based on the targets proposed by the Licensees. Licensees have to come up with proposals in a time frame fixed by the Commission. |
| CAIFI |  |
| CAIDI |  |

CHAPTER - 6

GUARANTEED STANDARDS OF PERFORMANCE FOR TRANSMISSION

- Voltage Variation

- Voltage Variation is defined as the derivation of the root mean square (RMS) value of the voltage from its nominal RMS value, expressed in terms of percentage. Voltage Variation may be either of short duration not exceeding one minute or of long duration for a time greater than one minute.

- For the purpose of these standards, the sustained variation in steady state voltage exceeding one-minute duration shall be considered. The specified permissible limits of sustained voltage variation shall not apply in the cases where the circumstances are reasonably beyond the control of State Transmission Utility. e.g. Major break-downs, grid failures, accidents, system distress conditions etc.

State Transmission Utility shall make all possible efforts to ensure that the grid voltages remain within the following voltage levels at all points of its Transmission System.

| Nominal Voltage (kV) | Maximum Value (kV) | Minimum Value (kV) |
| --- | --- | --- |
| 220 | 245 | 200 |
| 132 | 145 | 120 |
| 33 | 35 | 30 |
| 11 | 11.67 | 10 |

- 11 kV voltages to be maintained by the Transmission Licensee only in those cases where 11 kV supply is extended from the EHT sub-station.

- Frequency Variation

The State Transmission System operates as an integral part of the North-Eastern Regional Grid and frequency management is the joint responsibility of all the constituents in the North-Eastern Region.

The State Transmission Utility shall fulfil its obligation to enable the NERLDC to keep the frequency within specified ranges in accordance with provisions of IEGC:

The rated frequency of the system shall be 50.0 Hz

| Target Range(As per IEGC) | Variation (%) | Value (Hz) |
| --- | --- | --- |
| Upper Limit | +1% | 50.5 Hz |
| Lower Limit | -2% | 49.0 Hz |
| Statutory Acceptable Limit (As per IE Rules, 1956) | Variation (%) | Value (Hz) |
| Upper Limit | +3% | 51.5 Hz |
| Lower Limit | -3% | 48.5 Hz |
| Extreme conditions from system Security point of view | Variation (%) | Value (Hz) |
| Upper Limit | +5% | 52.5 Hz |
| Lower Limit | -5% | 47.5 Hz |

CHAPTER - 7

OVERALL STANDARDS OF PERFORMANCE FOR TRANSMISSION

- System Availability

- Feeder Availability:

- The feeder availability gives the percentage of time during which the feeder remained available for transmission. Feeder availability shall be calculated based on the following formula

| % Availability of Feeder = | (No. of feeders x 8760 – Annual outages in all feeder-hours) x 100 |
| --- | --- |
|  | No. of Feeders X 8760 |

Here, total availability in hours is equal to the number of hours in a year i.e., 8760

(Non leap year)

- The State Transmission Utility shall achieve 95% feeder availability from the

preliminary stage itself.

(b)  Sub-Station Availability:

- The sub-station availability expressed in percentage is the measure of the extent

the power transmission capacity remained available from a sub-station. Sub-station availability shall be calculated based on following formula:

| % Availability of SS = | (Installed capacity in MVA x 8760 - outage in MVA x Hours) x 100 |
| --- | --- |
|  | Installed capacity in MVA x 8760 |

(ii)	The State Transmission Utility shall achieve 95% Substation availability from the

preliminary stage itself.

(2)   Voltage Unbalance

Voltage Unbalance is defined as the maximum deviation in voltage between two phases

divided by the average of the phase voltages of all three phases, expressed in terms of

percent:

| Voltage Unbalance = | Deviation between highest and lowest phase voltage | X 100 |
| --- | --- | --- |
|  | Average voltage of three phases |  |

The phase voltages of a 3-phase supply should be of equal in magnitude and phase angle and the loads on each phase should be balanced. Deviations will result in decreased efficiency, negative torque, vibrations and overheating. Severe unbalance could lead to malfunctioning of some equipment. Some types of loads like X-ray machine, electric traction, induction & arc furnace may induce unbalance in the supply voltages.

The voltage unbalance at the inter-connection point with STU shall not exceed the values given below:

| Voltage Level | Limit of Voltage unbalance |
| --- | --- |
| 220 KV | 2% |
| 132 KV | 3% |

The Voltage unbalance shall be measured from hourly Log Sheet Data reordered at sub-stations. Voltmeter having accuracy class not more than 1% shall be preferably used for recording hourly readings.

(3) 	Neutral Voltage Displacement

- Unbalance in loads on three phases cause shifting of neutral from earth potential. Neutral displacement is applicable for transformers with 'Star Point' solidly grounded. Under "solidly" grounded conditions, the potential of neutral should be equal to earth i.e. zero. But in actual conditions, the earthing of the star point is imperfect and so the star to ground offers small resistance. This results in flow of negative sequence currents through neutral to ground. The neutral therefore shifts from earth potential.

- Unbalance voltages and displacement of neutral will result in decreased efficiency, negative torque, leakage currents, vibrations and overheating. Severe unbalance and neutral displacement could lead to malfunctioning of some equipment. Some types of loads like X-ray machines; electric traction; induction and arc furnace may induce unbalance in the supply voltages and shift the voltage of neutral from earth potential.

- The STU shall ensure that the neutral point voltage of the all EHV transformers with respect to earth will not have potential greater than 2% of the no load phase to phase voltage of the transformer.

(4) 	Voltage Variation Index (VVI)

- Voltage Variation Index representing the degree of voltage variation from nominal value over a specified period of time expressed as a standard deviation. The Voltage Variation Index (VVI) shall be computed from hourly Log Sheet Data reordered at sub-stations as per the following formula:

| N Σ (Vi - Vs)2 i=1 |  | X 100 |
| --- | --- | --- |
| N |  | Vs |

VV I =

Where,

Vi = RMS value of hourly measured voltage (in kV) at i th  hour in the period for

which VVI is computed;

Vs = RMS value of the nominal system voltage i.e. 400kV, 220kV, 132 kV etc. as

may be applicable at the interconnection point;

N = Number of hourly measurements over the specified period of time.

Note: The data from defective metering or any abnormal data shall be discarded from

calculations.

- VVI shall be completed on monthly basis.

- The Commission shall fix benchmark for standards of VVI on the basis of data

collected for at least one year and revise the levels to be achieved from time to time for ensuring improvement in the performance of STU. The VVI on annual basis shall not exceed the limit of 1% for Voltage levels of 220 KV and 132 KV.

(5)	Service Reliability:

The points where electric power is supplied from transmission system to the Users (Distribution Companies, another transmission system, EHV consumers) are called delivery points or interface points. Outage at these points directly affects the Users of the Grid. The reliability level at the delivery points is therefore an indication of quality of service provided by STU to its Users.

System reliability of the Grid is expressed in terms of:

- Consumer Average Interruption Frequency Index (CAIFI);

- Consumer Average Interruption Duration Index (CAIDI).

(a) 	Consumers Average Interruption Frequency Index (CAIFI)

This index gives number of interruptions in power supply to loads expressed as per year per EHV Sub-station for a voltage class. All interruptions except due to acts of nature (like earthquake, floods, storms etc.), fire, orders of civil/military authorities, scheduled outage, load shedding to meet capacity shortage, failure of PGCIL transmission system or failure of generating units (leading to grid failure or system islanding) of duration exceeding ten (10) minutes at a time shall be counted in computing the index.

CAIFI = R I / N

Where,

R I = Sum of number of interruptions exceeding 10 minutes at a time duration in the

year for the given voltage class;

N = Number of EHV sub-stations in service at the beginning of year having that class

of voltage supply.

CAIFI shall be computed for each voltage class separately.

(b) 	Consumers Average Interruption Duration Index (CAIDI)

This index gives weighted average interruptions in a year with reference to the total connected load on the system. All interrupted loads for duration exceeding ten (10) minutes at a time in the year are counted in computing the index. Interruptions due to acts of nature, orders of civil/military authorities, scheduled outage (including three shift operation of agriculture pump sets), load shedding to meet capacity shortage, failure of PGCIL transmission system or failure of generating units (leading to grid failure or system islanding) shall be however excluded in the computation of this index. CAIDI gives the measure of average interruption time per EHV Sub-station on annual basis for a voltage class.

CAIDI = R D / N

Where,

R D = Sum of duration of all interruptions of exceeding 10 minutes at a time in the

year for the given voltage class;

N = Number of EHV sub-stations in service at the beginning of year having that class

of voltage supply.

(6)	System Adequacy

System adequacy is the ability of the power system to receive the generated power or supply the aggregate electrical demand and energy requirements at all times, taking into account scheduled and reasonably expected unscheduled outage of     system elements.

The STU shall observe the Transmission Planning Criteria specified by Central Electricity Authority for designing, developing the transmission network. The Transmission Licensee shall observe the operational standards laid down by CEA Manual for Transmission Planning.

The system voltage and frequency shall be close to the nominal values as possible  and there shall be no overloading of any system element under normal conditions  and different feasible load-generation conditions.

The system voltage and frequency and loading of system elements shall remain  within prescribed limits and not necessitate load shedding or generation re-scheduling in the event of outage of any single system element over and above a pre-contingency system depletion of another element in another corridor.

The system shall remain in synchronism without necessitating load shedding or  islanding in the event of single–phase-ground fault or three-phase faults successful clearing of fault by isolating/opening of the faulted system elements. The system shall have adequate margins in terms of voltage and steady state oscillatory stability.

By Order of the Commission

P.SANI

Dy. Dir-cum-Commission Secretary,

NERC, Kohima.

#### Format – 1

Format for Furnishing information on Achieving level of

Performance and Guaranteed Standards

For Distribution ( Under Regulation 5.1 to 5.10)

Name of Licensee ………………………………………………………………….

Report for the quarter ending on …………………………/ for Financial Year …………………..

Number and Type of Complaints attended and balance to be attended.

| Sl. No. | Type of complaint | Pending complaints of previous quarter | Complaints received during the Quarter year | Total Complaints | No. of complaints redressed during the quarter |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | In stipulated time | Beyond Stipulated time | Total | Balance complaints to be redressed |
| 1 | Interruption of Supply |  |  |  |  |  |  |  |
| 2 | Voltage Related |  |  |  |  |  |  |  |
| 3 | Meter Related |  |  |  |  |  |  |  |
| 4 | New Connection where extension of distribution mains already exists |  |  |  |  |  |  |  |
| 5 | New connection where extension of distribution mains was required |  |  |  |  |  |  |  |
| 6 | New connection where commissioning of a new transformer was required. |  |  |  |  |  |  |  |
| 7 | Transfer of ownership and conversion of service |  |  |  |  |  |  |  |
| 8 | Complaints on Consumer's bill |  |  |  |  |  |  |  |
| 9 | Reconnection of Supply |  |  |  |  |  |  |  |
| 10 | Others |  |  |  |  |  |  |  |

##### Format – 2

Format for Furnishing information on Achieving level of performance and

Guaranteed standards for Distribution (Under Regulation 5.1 to 5.10)

Name of Licensee ………………………………………………………………….

Report for the quarter ending on …………………………/ for Financial Year …………………..

Number of cases where compensation paid & amount of compensation paid

| Sl. No | Type of Complaints | No. of Cases where compensation was payable | No. of cases where compensation was paid | Total amount (in Rs. of the compensation paid) |
| --- | --- | --- | --- | --- |
| 1 | Interruption of Supply |  |  |  |
| 2 | Voltage Related |  |  |  |
| 3 | Meter Related |  |  |  |
| 4 | New Connection where extension of distribution mains already exists |  |  |  |
| 5 | New connection where extension of distribution mains was required |  |  |  |
| 6 | New connection where commissioning of a new transformer was required. |  |  |  |
| 7 | Transfer of ownership and conversion of service |  |  |  |
| 8 | Complaints on Consumer's bill |  |  |  |
| 9 | Reconnection of Supply |  |  |  |
| 10 | Others |  |  |  |

#### Format – 3

Format for Furnishing information on Achieving level of performance and Overall standards for Distribution

Name of Licensee ………………………………………………………………….

Report for the quarter ending on …………………………/ for Financial Year …………………..

(a) Percentage of performance achieved on overall standards

| Sl. No. | Service area covered under this standard | Targeted Performance | Performance Achieved |
| --- | --- | --- | --- |
| 1 | Fuse off calls | 95% |  |
| 2 | Line Break Downs | 95% |  |
| 3 | Replacement of failed distribution transformers | 95% |  |
| 4 | Period of scheduled outages | 95% |  |
| 5 | Street light faults | 90% |  |
| 6 | Resolving Billing Mistakes | 99% |  |
| 7 | Replacing of Faulty Meters | 95% |  |
| 8 | Reliability Indices | Target will be furnished separately |  |
|  | (a) CAIFI |  |  |
|  | (b) CAIDI |  |  |

- Measures taken to improve performance in the areas covered in Overall standards Brief note to be furnished by the Licensee

# Format - 5

# HALF YEARLY REPORT ON TRANSMISSION PERFORMANCE STANDARDS

NAME OF STATE TRANSMISSION UTILITY …………………………………………………………

Report for half year ending: 			(For the Financial Year ______________)

| Sl. No | Category of Standard | Performance Standards (s) | Actual Achievement for half year |
| --- | --- | --- | --- |
| 1 (a) | Feeders availability | 95% |  |
| (b) | Substation availability | 95% |  |
| 2 | Voltage unbalance |  |  |
| (a) | 220 kV | 2% |  |
| (b) | 132 kV | 3% |  |
| 3 | Neutral voltage displacement | 2% |  |
| 4 | Voltage variation index |  |  |
| (a) | 220 kV | 1% |  |
| (b) | 132 kV | 1% |  |
| 5 | Service reliability |  |  |
| (a) | CAIFI | To be laid down by the Commission based on targets proposed by the licensee |  |
| (b) | CAIDI |  |  |

Note:

1.	The State Transmission Utility shall maintain the base data like Log Sheet, Complaint Register and Interruption Register etc. at sub-station level.

- For compilation of monthly report at circle level base data of sub-stations shall be used.

- The consolidated report for whole State Transmission Utility/Transmission Licensee shall be based on circle – wise compilation.

- The circle - wise compilation and base data at sub-station level may be subject to Commission scrutiny as may be necessary.